## HE calc
Heat Exchanger Calculations E510
Table-A: Energy unit conversion
1 | Btu | 1055 | J |  |  | Substance |  | Cp (J/kgdegC) | Cp(Btu/lb.degF)
|  | 1.055 | kJ |  |  | Alcohol, ethyl 32oF (ethanol) |  | 2.3 | 0.55
|  | 0.2521 | kcal |  |  | Ammonia, 104oF |  | 4.86 | 1.16
|  | 107.7 | Kgf.m |  |  | Castor Oil |  | 1.8 | 0.43
|  | 778.7 | ft.lbf |  |  | Dowtherm |  | 1.55 | 0.37
1 | cal | 4.18 | J |  |  | Freon R-12 saturated 0oF |  | 0.91 | 0.217
|  | 0.00396 | Btu |  |  | Fuel Oil max. |  | 2.09 | 0.5
|  | 1.16e-06 | kW.h |  |  | Gasoline |  | 2.22 | 0.53
1 | kcal | 3.9604 | Btu
Table-B: Power unit conversion | [5 empty] | Heptane |  | 2.24 | 0.535
1 | W | 0.001 | kW |  |  | Kerosene |  | 2.01 | 0.48
|  | 0.00134 | hp |  |  | Gold |  | 0.129 | 0.0308
|  | 0.000102 | hp (boiler) |  |  | Light Oil, 60oF |  | 1.8 | 0.43
|  | 0.0002387 | kcal/s |  |  | Light Oil, 300oF |  | 2.3 | 0.54
|  | 0.102 | kgf.m/s |  |  | Mercury |  | 0.14 | 0.03
|  | 0.7375 | ft.lbf/s |  |  | Octane |  | 2.15 | 0.51
|  | 44.2 | ft.lbf/min |  |  | Oil, mineral |  | 1.67 | 0.4
|  | 0.000948 | Btu/s |  |  | Olive oil |  | 1.97 | 0.47
|  | 0.000284 | ton (refrig) |  |  | Petroleum |  | 2.13 | 0.51
Table-C: Pressure unit conversion | [5 empty] | Propane, 32oF |  | 2.4 | 0.576
Unit | Pascal | bar | atmosphere | Torr | pound per square inch | Propylene Glycol |  | 2.5 | 0.6
| (Pa) | (bar) | (atm) | (Torr) | (psi) | Sodium chloride |  | 3.31 | 0.79
[6 empty] | Soya bean oil |  | 1.97 | 0.47
1 Pa | 1 N/m² | 1e-05 | 9.867e-06 | 0.0075006 | 0.000145 | Toluene |  | 1.72 | 0.41
1 bar | 100000 | 106 dyn/cm2 | 0.9867 | 750 | 14.5 | Water, fresh |  | 4.19 | 1
1 at | 98066 | 0.98067 | 0.968 | 735.5 | 14.223 | Water, sea 36oF |  | 3.93 | 0.94
1 atm | 101325 | 1.0132 | 1 atm | 760 | 14.7
1 torr | 133.322 | 0.013332 | 0.0013158 | 1 mmHg | 0.0193
1 psi | 0.006894 | 0.068948 | 0.068046 | 51.72 | 1 lbf/in²
Table-1: Calculation of required heat transfer rate (CW side)
Q=m.Cp.(T2-T1)
where,
Q= | heat transfer rate | Gcal/h | 18.483
m= | mass flow rate | kg/hr | 1852000
Cp= | Specific heat of substance | j/kg.degC | 0.998
T2-T1= | Change in Temp | degC | 10
Table-2 Calculation of Log mean Temp Difference, LMTD, ΔTm for obtaining surface Area
ΔTm = | [(T1 – t2) – (T2 – t1)]/ln{(T1 – t2)/(T2 – t1)}
where,
Q = | Heat transfer rate (kJ/h) (Btu/h)
T1 = | Inlet hot fluid temp. | degC | 121
t2 = | Outlet cold fluid temp | degC | 45
T2 = | Outlet hot fluid temp | degC | 43
t1 = | Inlet cold fluid temp | degC | 35
Tm | Ave shell side temp | degC | 82
ΔT1= | (T1 – t2) | degC | 76
ΔT2= | (T2 – t1) | degC | 8
Numerator | [(T1 – t2) – (T2 – t1)] | [(35-43)-(45-121)] | 68
Denominator | ln{(T1 – t2)/(T2 – t1)} | ln[(35-43)/(45-121)] | 2.2513
ΔTm = |  |  | 30.2049
Fouling factor vapour side |  | h.m2.K/Kcal | 0.0002
Fouling factor liquid side |  | h.m2.K/Kcal | 0.0004
Table-3: Calculation of Tube side heat transfer co-efficient
Tubular exchanger parameters
|  |  |  | 1st pass | 2nd pass
No of tubes |  | nos | N | 1387 | 1388
OD of tube |  | mm | Do | 19.05
ID of tube |  | mm | Di | 14.83
X-sec area of ID |  | mm2 |  | 172.6442
|  | m2 |  | 0.00017264
|  | shell side |  | tube side
|  | in | out | in | out
Flow | Kg/hr | 59891 | 1774+60 | 1852000 | 1852000
| m3/hr |  |  | 1852 | 1852
| m3/s |  |  | 0.51444 | 0.51444
Flow velocity,u
| m/s |  |  | 2.1484
Sp heat, Cp | kcal/kg0C |  |  | 0.997 | 0.997
Cp | j/kg0C |  |  | 4171.448 | 4171.448
conduct, kfb | kcal/h.m.oC |  |  | 0.541 | 0.541
| w/m.oC |  |  | 0.62918 | 0.62918
Effective Length of tube |  |  | L | 12200 | mm
Renold's no (tube side) |  | Di*u*ρ/μ | Ret= | 47850.8948
|  | Fluid Velocity | u (m/s) | 2.1484
|  | density at ave temp | ρ (kg/m3) | 992
|  | viscosity at ave temp | μ (CP) | 0.6605
|  | viscosity at ave temp | μ (kg/m.s) | 0.0006605
|  | viscosity at ave temp | μ (mPa/m.s) | 0.6605
|  | sp heat | Cp (j/kgoC) | 4171.448
|  | Conductivity | kfb (w/m.oC) | 0.62918
Prandtl No (tube side) | Prt | Cp*μ/kfb | Prt= | 4.3791
Nut=(f/2)*Ret*Prt/[1.07+12.7(f/2)^.5*(Prt^2/3-1)] where f=(1.58lnRet-3.28)^-2
|  | f= |  | 0.0052925
|  | f/2 |  | 0.0026462
|  | Nut |  | 120.7347
Check of applicability of Equation [ Re>2100 and μ<2]
|  | Re | > | 2100
|  | μ | < | 2
|  | Both satisfies | therefore formula can be applied
Nusselt no (tube side) |  |  | Nu= | 120.7347
Calculating hi with this value of Nu
|  | hi=Nu*kfb/Di | hi= | 5122.3334 | W/m2.degC
Heat transfer rate |  | Q=mCp(T2-T1)
ΔTm= | degK
Surface Area, A= |  | Q/(U*ΔTm)
|  |  |  | CS | SS
Q= | Gcal/h |  |  | 18 | 27.7244
Q= | Kcal/h |  |  | 18000000 | 27724440
ΔTm= | degK |  |  | 30.2049 | 30.2049
U= | W/m2*K |  |  | 359 | 680
U= | Kcal/m2*h*K |  |  | 308.74 | 584.8
Uf | Kcal/m2*h*K |  |  | 260.4864 | 432.903
A= | m2 |  |  | 2287.7589 | 2120.289
15.75
[6 empty] | Ln (Do/Di)/2pikL | Num | 0.25041 | 14.83
[6 empty] | CS | Deno |  | 11067181.2
[7 empty] | ratio |  | 1.34e-06
[6 empty] | Ln (Do/Di)/2pikL | Num | 0.19023 | 15.75
[6 empty] | SS | Deno |  | 1103.2704
[7 empty] | ratio |  | 0.014276
Shell side calculations
Cross sectional area
Pitch |  | p | mm | 25.4
ID of the shell |  |  | mm | 1448
No of Tubes in single pass |  |  | Nos | 1387
OD of Tube |  | do | mm | 19.05
X-sec Area covered by Tubes in single pass |  |  | mm2 | 395126.4275
X-sec Area covered by ID of shell |  |  | mm2 | 1645912.64
X-sec Area of shell excluding tubes |  |  | mm2 | 1250786.2125
|  |  | m2 | 1.2508
Flow in shell side |  |  | kg/hr | 59891
Density of vapour |  |  | kg/m3 | 12.2799
Volumetric flow in shell side |  |  | m3/hr | 4877.157
|  |  | m3/s | 1.3548
Velocity of vapour |  |  | m/s | 1.0831
Equivalent Diameter, De
De= | 4*Free flow area
wetted preimeter
| 4*(p^2*3^.5/4-3.14*do^2/8) |  | mm | 18.3112
3.14*do/2
Bundle cross flow area, As |  |  | Ds (mm)= | 1448
|  |  | P (mm)= | 25.4
As (mm2)= | C*B*Ds/P | 157470 | C (mm)= | 6.35
|  |  | B (mm)= | 435
where | C=P-do
B=baffle spacing
Shell side Reynold's Number, Res
Res= | (ms/As)*(De/μs)
where | ms=flow rate shell side |  | kg/s | 16.6364
| As=bundle cross flow area |  | m2 | 0.15747
| De=Equivalent dia of shell side |  | m | 0.018311
| μs=viscosity of shell side fluid |  | kg/m.s | 1.2061e-05
Res= |  |  |  | 160401.131
Prandtl No, Pr |  | Cp*μ/kfb
where | Cp= sp heat |  | J/kg.K | 2910.8752
| c=viscosity at mean temp |  | kg/m.s | 1.2061e-05
| kfb=conductivity at mean temp |  | W/m*K | 0.03537
| Pr= |  |  | 0.99257
Calculation of film heat transfer coeff in shell side, ho
| ho= | 0.36*ks*Res^.55*Pr^1/3/(De)
The equation holds good if
|  | 2100>Res>1*10^6 | 160401.131 | Satisfies
| ho= | 505.8301 | W/m2.degC
Calculation of overall heat transfer
Film HT coeff | hi= | 5122.3334 | W/m2.degC | 0.00019522
| (Ao/Ai)*hi= |  |  | 0.00025078
Film HT coeff | ho= | 505.8301 | W/m2.degC | 0.0019769
| (Ao/Ai)*ho= |  |  | 0.0025395
Resist.of wall | (Ao/Ai)*ro*Ln (ro/ri)/k | 5.547e-05 | K/W | 5.547e-05
Fouling resist shell side, Rfi= |  | 0.0004 | h.m2.K/kcal | 0.00034423
| (Ao/Ai)*Rfi= | 0.00034423 | m2.K/W | 0.00044219
Fouling resist tube side, Ro= |  | 0.0002 | h.m2.K/kcal
| Ro= | 0.00017212 | m2.K/W | 0.00017212
0.0032879
Resistance | 1/Uc= | 5.982e-08 |  | 304.1418
Fouled resistance |  | 0.00051641
| Uc | 1936.4423 | W/m2.K
Surface Area, A= |  | Q/(U*ΔTm)
|  |  |  | CS | SS
Q= | Gcal/h |  |  | 18 | 27.7244
Q= | Kcal/h |  |  | 18000000 | 27724440
ΔTm= | degK |  |  | 30.2049 | 30.2049
U= | W/m2*K |  |  | 359 | 680
U= | Kcal/m2*h*K |  |  | 308.74 | 584.8
Uf | Kcal/m2*h*K |  |  | 260.4864 | 432.903
A= | m2 |  |  | 2287.7589 | 2120.289

## thermal cond
Metal, Metallic Element or Alloy | Temperature | Thermal Conductivity
| - t - | - k -
| (oC) | (W/m K)
Aluminum | -73 | 237
" | 0 | 236
" | 127 | 240
" | 327 | 232
" | 527 | 220
Aluminum - Duralumin (94-96% Al, 3-5% Cu, trace Mg) | 20 | 164
Aluminum - Silumin (87% Al, 13% Si) | 20 | 164
Aluminum bronze | 0 - 25 | 70
Aluminum alloy 3003, rolled | 0 - 25 | 190
Aluminum alloy 2014. annealed | 0 - 25 | 190
Aluminum alloy 360 | 0 - 25 | 150
Antimony | -73 | 30.2
" | 0 | 25.5
" | 127 | 21.2
" | 327 | 18.2
" | 527 | 16.8
Beryllium | -73 | 301
" | 0 | 218
" | 127 | 161
" | 327 | 126
" | 527 | 107
" | 727 | 89
" | 927 | 73
Beryllium copper 25 | 0 - 25 | 80
Bismuth | -73 | 9.7
" | 0 | 8.2
Boron | -73 | 52.5
" | 0 | 31.7
" | 127 | 18.7
" | 327 | 11.3
" | 527 | 8.1
" | 727 | 6.3
" | 927 | 5.2
Cadmium | -73 | 99.3
" | 0 | 97.5
" | 127 | 94.7
Cesium | -73 | 36.8
" | 0 | 36.1
Chromium | -73 | 111
" | 0 | 94.8
" | 127 | 87.3
" | 327 | 80.5
" | 527 | 71.3
" | 727 | 65.3
" | 927 | 62.4
Cobalt | -73 | 122
" | 0 | 104
" | 127 | 84.8
Copper | -73 | 413
" | 0 | 401
" | 127 | 392
" | 327 | 383
" | 527 | 371
" | 727 | 357
" | 927 | 342
Copper, electrolytic (ETP) | 0 - 25 | 390
Copper - Admiralty Brass | 20 | 111
Copper - Aluminum Bronze (95% Cu, 5% Al) | 20 | 83
Copper - Bronze (75% Cu, 25% Sn) | 20 | 26
Copper - Brass (Yellow Brass) (70% Cu, 30% Zn) | 20 | 111
Copper - Cartridge brass (UNS C26000) | 20 | 120
Copper - Constantan (60% Cu, 40% Ni) | 20 | 22.7
Copper - German Silver (62% Cu, 15% Ni, 22% Zn) | 20 | 24.9
Copper - Phosphor bronze (10% Sn, UNS C52400) | 20 | 50
Copper - Red Brass (85% Cu, 9% Sn, 6%Zn) | 20 | 61
Cupronickel | 20 | 29
Germanium | -73 | 96.8
" | 0 | 66.7
" | 127 | 43.2
" | 327 | 27.3
" | 527 | 19.8
" | 727 | 17.4
" | 927 | 17.4
Gold | -73 | 327
" | 0 | 318
" | 127 | 312
" | 327 | 304
" | 527 | 292
" | 727 | 278
" | 927 | 262
Hafnium | -73 | 24.4
" | 0 | 23.3
" | 127 | 22.3
" | 327 | 21.3
" | 527 | 20.8
" | 727 | 20.7
" | 927 | 20.9
Hastelloy C | 0 - 25 | 12
Inconel | 21 - 100 | 15
Incoloy | 0 – 100 | 12
Indium | -73 | 89.7
" | 0 | 83.7
" | 127 | 75.5
Iridium | -73 | 153
" | 0 | 148
" | 127 | 144
" | 327 | 138
" | 527 | 132
" | 727 | 126
" | 927 | 120
Iron | -73 | 94
" | 0 | 83.5
" | 127 | 69.4
" | 327 | 54.7
" | 527 | 43.3
" | 727 | 32.6
" | 927 | 28.2
Iron - Cast | 20 | 52
Iron - Nodular pearlitic | 100 | 31
Iron - Wrought | 20 | 59
Lead | -73 | 36.6
" | 0 | 35.5
" | 127 | 33.8
" | 327 | 31.2
Chemical lead | 0 - 25 | 35
Antimonial lead (hard lead) | 0 - 25 | 30
Lithium | -73 | 88.1
" | 0 | 79.2
" | 127 | 72.1
Magnesium | -73 | 159
" | 0 | 157
" | 127 | 153
" | 327 | 149
" | 527 | 146
Magnesium alloy AZ31B | 0 - 25 | 100
Manganese | -73 | 7.17
" | 0 | 7.68
Mercury | -73 | 28.9
Molybdenum | -73 | 143
" | 0 | 139
" | 127 | 134
" | 327 | 126
" | 527 | 118
" | 727 | 112
" | 927 | 105
Monel | 0 – 100 | 26
Nickel | -73 | 106
" | 0 | 94
" | 127 | 80.1
" | 327 | 65.5
" | 527 | 67.4
" | 727 | 71.8
" | 927 | 76.1
Nickel - Wrought | 0 – 100 | 61 – 90
Cupronickel 50 -45 (Constantan) | 0 - 25 | 20
Niobium (Columbium) | -73 | 52.6
" | 0 | 53.3
" | 127 | 55.2
" | 327 | 58.2
" | 527 | 61.3
" | 727 | 64.4
" | 927 | 67.5
Osmium | 20 | 61
Palladium |  | 75.5
Platinum | -73 | 72.4
" | 0 | 71.5
" | 127 | 71.6
" | 327 | 73
" | 527 | 75.5
" | 727 | 78.6
" | 927 | 82.6
Plutonium | 20 | 8
Potassium | -73 | 104
" | 0 | 104
" | 127 | 52
Red brass | 0 - 25 | 160
Rhenium | -73 | 51
" | 0 | 48.6
" | 127 | 46.1
" | 327 | 44.2
" | 527 | 44.1
" | 727 | 44.6
" | 927 | 45.7
Rhodium | -73 | 154
" | 0 | 151
" | 127 | 146
" | 327 | 136
" | 527 | 127
" | 727 | 121
" | 927 | 115
Rubidium | -73 | 58.9
" | 0 | 58.3
Selenium | 20 | 0.52
Silicon | -73 | 264
" | 0 | 168
" | 127 | 98.9
" | 327 | 61.9
" | 527 | 42.2
" | 727 | 31.2
" | 927 | 25.7
Silver | -73 | 403
" | 0 | 428
" | 127 | 420
" | 327 | 405
" | 527 | 389
" | 727 | 374
" | 927 | 358
Sodium | -73 | 138
" | 0 | 135
Solder 50 - 50 | 0 - 25 | 50
Steel - Carbon, 0.5% C | 20 | 54
Steel - Carbon, 1% C | 20 | 43
Steel - Carbon, 1.5% C | 20 | 36
" | 400 | 36
" | 122 | 33
Steel - Chrome, 1% Cr | 20 | 61
Steel - Chrome, 5% Cr | 20 | 40
Steel - Chrome, 10% Cr | 20 | 31
Steel - Chrome Nickel, 15% Cr, 10% Ni | 20 | 19
Steel - Chrome Nickel, 20% Cr, 15% Ni | 20 | 15.1
Steel - Hastelloy B | 20 | 10
Steel - Hastelloy C | 21 | 8.7
Steel - Nickel, 10% Ni | 20 | 26
Steel - Nickel, 20% Ni | 20 | 19
Steel - Nickel, 40% Ni | 20 | 10
Steel - Nickel, 60% Ni | 20 | 19
Steel - Nickel Chrome, 80% Ni, 15% Ni | 20 | 17
Steel - Nickel Chrome, 40% Ni, 15% Ni | 20 | 11.6
Steel - Manganese, 1% Mn | 20 | 50
Steel - Stainless, Type 304 | 20 | 14.4
Steel - Stainless, Type 347 | 20 | 14.3
Steel - Tungsten, 1% W | 20 | 66
Steel - Wrought Carbon | 0 | 59
Tantalum | -73 | 57.5
" | 0 | 57.4
" | 127 | 57.8
" | 327 | 58.9
" | 527 | 59.4
" | 727 | 60.2
" | 927 | 61
Thorium | 20 | 42
Tin | -73 | 73.3
" | 0 | 68.2
" | 127 | 62.2
Titanium | -73 | 24.5
" | 0 | 22.4
" | 127 | 20.4
" | 327 | 19.4
" | 527 | 19.7
" | 727 | 20.7
" | 927 | 22
Tungsten | -73 | 197
" | 0 | 182
" | 127 | 162
" | 327 | 139
" | 527 | 128
" | 727 | 121
" | 927 | 115
Uranium | -73 | 25.1
" | 0 | 27
" | 127 | 29.6
" | 327 | 34
" | 527 | 38.8
" | 727 | 43.9
" | 927 | 49
Vanadium | -73 | 31.5
" | 0 | 31.3
" | 427 | 32.1
" | 327 | 34.2
" | 527 | 36.3
" | 727 | 38.6
" | 927 | 41.2
Zinc | -73 | 123
" | 0 | 122
" | 127 | 116
" | 327 | 105
Zirconium | -73 | 25.2
" | 0 | 23.2
" | 127 | 21.6
" | 327 | 20.7
" | 527 | 21.6
" | 727 | 23.7
" | 927 | 25.7
Thermal Conductivity Online Converter